# PLC Signal Testing Workflow

Use this procedure after connecting the test computer to the anodizing-line PLC Wi-Fi network.

| 1. Get API Details | 2. Test API Connection | 3. Configure Console | 4. Start Backend | 5. Verify Live Data | 6. Enable Write Testing |
| --- | --- | --- | --- | --- | --- |

| 1 | Get the PLC API connection details |
| --- | --- |

PLC / gateway IP address and port (example: http://192.168.1.100:8000)

PLC API key

Confirm the actual PLC/gateway IP with the supplier. The supplier documentation only shows 127.0.0.1:8000 as a local example.

Authentication header: X-API-Key

| 2 | Test the supplier API from a terminal |
| --- | --- |

Do this before changing the PLC Test Console. If these commands fail, the UI will not be able to communicate with the PLC either.

COMMAND 1 - READ TAG CATALOG

curl -H "X-API-Key: YOUR_KEY" \ http://192.168.1.100:8000/api/v1/tags/list

Expected result: The API returns the PLC tag list and metadata.

COMMAND 2 - READ LIVE PLC VALUES

curl -H "X-API-Key: YOUR_KEY" \ http://192.168.1.100:8000/api/v1/tags/read

Expected result: The API returns the latest PLC signal values and poll information.

| 3 | Configure the PLC Signal Test Console |
| --- | --- |

CONFIGURATION - .ENV

PLC_API_BASE_URL=http://192.168.1.100:8000 PLC_API_KEY=YOUR_API_KEY PLC_MOCK_MODE=false

Expected result: Mock mode is disabled and the console points to the real supplier API.

| 4 | Start the local backend |
| --- | --- |

COMMAND - START BACKEND

uvicorn server.app:app --host 0.0.0.0 --port 8080

OPEN IN BROWSER

http://127.0.0.1:8080

| 5 | Confirm that the UI is connected to the real PLC |
| --- | --- |

Expected result: The UI must no longer show MOCK MODE.

EXPECTED UI STATUS

PLC API CONNECTED PLC MODE REMOTE DATA FRESH TAGS OK xxx / 0

Important: Confirm that the PLC is in REMOTE / API MODE before attempting write tests.

| 6 | Verify read signals first, then enable controlled write testing |
| --- | --- |

Keep the console in READ-ONLY MODE at first.

Compare values shown in Live Signals / Raw Tags with the supplier HMI or Swagger UI.

COMPARE

PLC HMI / Swagger value ↕ PLC Signal Test Console value

Expected result: The same signal should show the same value on both sides.

Only after the read values are confirmed: Enable write test mode → Manual write / Verification

RECOMMENDED FIRST COMMAND / FEEDBACK TEST

WRITE Tank01_DoorOpenRemote = 1 ↓ READ Tank01_DoorOpened = 1 ↓ PHYSICAL CHECK: Tank 01 door is actually open

Expected result: PASS only when the write is accepted, the feedback changes correctly, and the physical door actually opens.

If the terminal test in Step 2 fails

Stop here and check: PLC API IP/port, Wi-Fi routing, firewall settings, and whether the supplier API service is running. Do not troubleshoot the UI until the API itself is reachable.

Quick readiness checklist

| ☐ Connected to PLC Wi-Fi | ☐ PLC_MOCK_MODE=false |
| --- | --- |
| ☐ Correct PLC API IP and port confirmed | ☐ UI shows CONNECTED / REMOTE / FRESH |
| ☐ API key confirmed | ☐ Read values match supplier HMI / Swagger UI |
| ☐ tags/list works from terminal | ☐ Write test mode enabled only when ready |
| ☐ tags/read works from terminal |  |